Air Filters—1.0 General

1.1 - Air filters shall be high-efficiency, individually tested and certified panel filters consisting of aluminum enclosing frame, low-outgassing sealant, continuous thermoplastic resin pleat separators and micro glass media filter pack.

1.2 - Sizes shall be as noted on drawings or other supporting materials.

2.0 Construction

2.1 - Filter shall be manufactured in a facility qualified to IOS 9001-2015 Certified Quality System.

2.2 - Filter media shall be one continuous pleating of micro glass fiber media formed into a uniform pack depth of (53, 70, 100)* MM.

2.3 - Pleat spacing shall be by continuous thermoplastic resin separators to prevent media-to-media contact and promote uniform airflow through the media pack.

2.4 -The media pack shall be completely encapsulated in a polyurethane sealant creating a rigid self-supporting pack. The sealant shall be low out gassing and fire resistant.

2.5 -The enclosing frame, of anodized aluminum profiles, shall be joined together with secure internal corner clips to form a rugged and durable enclosure. Overall dimensional tolerance shall be correct within +0, -1/8”, and square within 1/4”.

2.6 - Gaskets, unless otherwise noted, shall be low outgassing cleanroom grade cellular urethane foam. Corners shall be continuously poured and jointless to form a leak-free, positive seal.

2.7 - Filters shall be listed per Underwriters Laboratories as UL 900.

3.0 Performance

3.1 - The filter shall be identified with a machine-printed (not handwritten) label including serial number, bar code, and actual tested efficiency, pressure drop, and airflow according to IEST-RP-CC001, latest edition.

3.2 - Manufacturer shall provide evidence of facility certification to ISO 9001:20015.

Units shall be Camfil Megalam Series or equal.

* Items in parentheses ( ) require selection.